## Document Information
Document Number | Author | Date | Version | Equipment Model # | I/O Manual Number
100-PBJ1226-PAA | Dhanya Sankaran | 2018-02-26 | Initiial Relase Version V1.0 | RES-DCVC60kW-480 | 100-PBJ1279-PAA

## Settings - General
Register Address | Variables | Signal from display menu | Scaling | Range | Default
#GENERAL SETTINGS
41024 | security_code | Security code |  | No Access = 0 Allow access=125 | 0
41025 | Heartbeat | Comm Timer | 1 / 0.1 s | 0 - 1000 | 1000

## Settings - DC
Register Address | Variables | Signal from display menu | Scaling | Range (Raw Values w/o scaling) | Default (Raw Values w/o scaling)
#DC SETTINGS 1
41026 | K_op_mode | Op Mode |  | Off=0, Constant voltage = 4 | 0
41027 | Op_mode_setpoint (Voltage reference) | Op mode Setpoint | Voltage scaling 32.767/V
41028 | bat_max_volt | Battery Voltage Max | 32.767/V | 400 - 840 V
41029 | bat_min_volt | Battery Voltage Min | 32.767/V | 270 - 400 V
41030 | bat_max_chrg_crt | Battery Max Charge Current | 52.094/A | 0 - -222 A
41031 | bat_max_dischrg_crt | Battery Max Discharge Current | 52.094/A | 0 - 222 A
41032 | bat_max_chrg_power | Battery Max Charge Power | 218.44/kW | 0 - 60 kW

## Settings - AC
Register Address | Variables | Signal from display menu | Scaling | Range (Raw Values w/o scaling) | Default (Raw Values w/o scaling)
#AC SETTINGS GRID MODE
41033 | ov_limit1_value | Grid Over Voltage Limit 1 | 32.767/V | 294 - 304.7 (V) | 304.7 V
41034 | ov_limit2_value | Grid Over Voltage Limit 2 | 32.767/V | 304.7 - 335.0 (V) | 321.3 V
41035 | uv_limit1_value | Grid Under Voltage Limit 1 | 32.767/V | 243.8 - 263.2 (V) | 243.8 V
41036 | uv_limit2_value | Grid Under Voltage Limit 2 | 32.767/V | 138.5 - 243.8 (V) | 138.5 V
41037 | of_limit1_value | Grid Over Frequency Limit 1 | 65.535/Hz | 60.0 - 60.5 (Hz) | 60.5 Hz
41038 | uf_limit1_value | Grid Under Frequency Limit 1 | 65.535/Hz | 59.3 - 60.0 (Hz) | 59.3 Hz
41039 | ov_tt_condn1_value | Over Voltage Trip Timing 1 | None | 30 -1900 (ms) | 1900 ms
41040 | ov_tt_condn2_value | Over Voltage Trip Timing 2 | None | 30 -160 (ms) | 140 ms
41041 | uv_tt_condn1_value | Under Voltage Trip Timing 1 | None | 30 -1900 (ms) | 1900 ms
41042 | uv_tt_condn2_value | Under Voltage Trip Timing 2 | None | 30 -160 (ms) | 140 ms
41043 | of_tt_condn1_value | Over Frequency Trip Timing | None | 30 -160 (ms) | 140 ms
41044 | uf_tt_condn1_value | Under Frequency Trip Timing 1 | None | 10 - 30000 (ms) | 140 ms
41045 | uf_tt_condn2_value | Under Frequency Trip Timing 2 | None | 10 - 100 (ms) | 60 ms
41046 | K_inverter_powerup_delay | Inverter Reconnect Time | 100/1s | (1s to 300s) | 5 s

## Status - General
Register Address | Variables | Signal from display menu | Scaling | Range | Default (Raw Values w/o scaling) | Security
#GENERAL STATUS
30256 | epc_amb_temp | Ambient Temperature | 109.22/c
30257 | hs_temp | Heat Sink Temperature | 109.22/c
30258 | modbus_address | Modbus Address
30259 | modbus_baudrate | Modbus Baudrate
30260 | modbus_parity | Modbus Parity
30261 | modbus_mode | Modbus Mode
30262 | modbus_timer | Comm Timer Count | 1 / 0.1s | 0-1000

## Status - DC
Register Address | Variables | Signal from display menu | Scaling | Range | Default | Security
#DC STATUS 1
30263 | dc_input_volt | Battery (Remote voltage) | 32.767/V
30264 | Voltage_ref_command | DC Link Setpoints | Voltage scaling 32.767/V
30265 | epcl_dc_link_volt | DC Bus Voltage | 32.767/V
30266 | epcl_dc_link_pwr | DC Bus Power | 218.44/kW
30267 | epc1_dc_link_crnt | DC Bus Current | 32.767/A
30285 | Power_lim_inverter | Power_limit | 218.44/kW

## Status -AC
Register Address | Variables | Signal from display menu | Range | Default | Scaling | Security
#GRID AC STATUS
30268 | ready to charge | ready to charge |  |  | 0/1
30269 | pha_load_volt_rms | Phase A Voltage RMS |  |  | 65.535/V
30270 | phb_load_volt_rms | Phase B Voltage RMS |  |  | 65.535/V
30271 | phc_load_volt_rms | Phase C Voltage RMS |  |  | 65.535/V

## CIU Faults and Warnings
Register Address | Variables | Signal from display menu | Scaling
30272 | ss_status[0] | CIU Fault | 0 . Critical Communication Error
1. Key Faulted
2. Control Values Receipt Failure
3. Modbus Communication Failed
4. Controller Mode Incorrect
5. Enclosure Overtemperature detected
6. CCU Faulted
7. Non CCU shuts
8. EPO shutdown
13. Lvps low fault
14. Low vbattery fault
15. Ambient temperature sensor oor shut

## MIU Faullts and Warnings
Register Address | Variables | Signal from display menu | Scaling
30273 | epcl_ss_status[0] | MIU Fault | 0 - Phase Out Under-Voltage
1 - Phase Out Over-Voltage
2 - Heatsink OverTemp fault
3 - Array Overvoltage fault
4 - Dc Link Overvoltage fault
5 - DC Bus Hardware Fault
7 - Software processing shutdown
8 - Unit Response Timeout
9 - Current Limit timeout shutdown
10 - Critical communication fault
11 - Offset Ir Shutdown
12 - Offset Is Shutdown
13 - K1 Failure to Close
14 - K1 Welded
15 - EPO Shutdown
30274 | epcl_ss_status[1] | MIU fault | 0 - Heatsink TempSensor fault
1 - Unexpected DC Bus fault
3 - DC Bus OverCurrent Shutdown
4 - Thermal OverLoad Shutdown
5 - Heatsink TempSense Dislocated fault
8 - DC Input Reverse Polarity Shutdown
9 - DC Bus Reverse Power Fault
13 - Precharge Fail Shutdown
14- DC Contactor Welded fault
15 -DC Contactor Open fault
30275 | epcl_additional_status[0] | Additional MIU Faullts | 0- Flash checksum shutdwn
1- Wrong initial voltage at startup shutdwn
2 - Single phase open shutdown
3- Sync error timeout shutdwn
4 - Grid phase seq reverse shutdwn
5- Inverter under freq shutdwn
6- Inverter over freq shutdwn
7- Lca grid hardware flt shutdown
8- Software over crnt shutdown
11- Program configuration invalid
12- Slave flt shutdwn
13- Power supply range shutdown
14 Ext_ad_a_shtdwn
15 Ext_ad_b_shtdwn
30276 | epcl_additional_status[1] | Additional MIU Faullts | 0 - Lca ovr curr shutdwn
1 - Lca dt fault shtdwn
2- Lca dc link overvoltage shtdwn
3- Lca ovr curr short shtdwn
4- Lca cneg fault shutdown
5- Lca cpos fault shutdown
6 - Lca bneg fault shutdown
7 - Lca bpos fault shutdown
8 - Lca aneg fault shutdown
9 - Lca_apos fault shutdown
10 - Lca ovrcur early shutdown
11 - Lca gnd fault shutdown
12 - Lca cp over temp shutdown
13 - Lca cp und temp shutdown
15 - Dc bus voltage out of range shtdwn
30277 | epcl_additional_status[2] | Additional MIU Faults | 1 - Dc link undervoltage shutdown
30278 | epcl_ss_status[2] | MIU Warnings
3- Power limited warning
8 - Over current short warning
9- Over current warning
13- Too cold warning
14- Heatsink overtemperature warning
15- EEPROM bad warning
30279 | epcl_ss_status[3] |  | 0 . Maintenance mode
1. Inverter switching
3. Connected to Grid
4. Positive DC contactor Status
5. Negative DC contactor Status
14. Cooling Fan on
15. CAN values received

## kWhrs
Register Address | Variables | Signal from display menu | Scaling
30280 | Dc_kwhr_1 | Dc_kwhr_1 | 92160000/kWhr
30281 | Dc_kwhr_2 | Dc_kwhr_2
30282 | Dc_kwhr_3 | Dc_kwhr_3
30283 | Dc_kwhr_4 | Dc_kwhr_4